|

|

|

|

|

|

|

|

|

|          ELECTRC7

|          --------

|          Copyright 1989, Robert J. La Capra

|          -------------------

|          All Rights Reserved

|

|

|

|

|

|

|

|

|

|

|          Robert J. La Capra

|          50 Hillside Terrace

|          Andover, NJ 07821

|

|

|

|

|

|

|

|

|

|

|

|

|

|

|

|

|

|

|

|

|

|

-- Table Of Contents --

Shareware ................................................ I

Disclaimer ............................................... II

Included Files ........................................... II

Introduction ............................................. 1

BOX FILL & SIZING

Device Box Fill Calculations ........................ 2

Junction, Pull Box Calculations

a. Straight Pull ............................... 3

b. Angle or U Pull ............................. 3

View Metal Box Table ................................ 3

CONDUIT SELECTOR ......................................... 4

GENERAL CALCULATIONS

Cost to Operate ..................................... 4

Ohm's Law Calcs ..................................... 5

LIGHTING CALCULATIONS (Zonal Cavity Method) .............. 5

MOTOR CALCULATIONS

Branch Conductor Sizing ............................. 8

Fuse or Breaker Sizing .............................. 8

Overload Protection Sizing .......................... 8

PIPE & WIRE SELECTOR AND COSTCOMP ........................ 9

REFERENCE TABLES

Equipment Grounding Conductor ....................... 11

Grounding Electrode Conductor ....................... 11

Killowatt - Ampere Conversion ....................... 11

Underground Cover Requirements ...................... 11

SETUP - COLOR AND DATABASE PRICES

Color Defaults ...................................... 11

Modify Database Prices .............................. 12

VOLTAGE DROP CALCULATOR .................................. 12

Registration ............................................. 14

Registration form ........................................ 15

=  Shareware  =

"Shareware" is a term used to describe a software distribution

method. Under the shareware concept, software may be freely copied

and passed along to others, or distributed through bulletin board

systems, shareware distributors, etc.

As a recipient of a shareware program, you may use the software

for a short trial period to determine if it meets your needs. If

it does, you pay the registration fee. By paying the fee, you are

granted the right to retain the software for your use. If the

software is not suitable then you are not obligated to pay the

fee, but you must not continue to use the program.

The shareware system provides substantial benefits to you.

1. You get to try out the software before you buy it.

2. Shareware is much less expensive than comparable commercial

packages. You don't pay for marketing and packaging.

3. Many programs have been developed by expert programmers who

would never consider marketing their products commercially.

All they ask in return is a small fee to compensate them for

all the time and effort they have invested in their products.

The system is based entirely on the honor system, and usually

works well. Most people are honest and wouldn't violate the trust

placed in them by the author of the software.

Shareware is not free software. The author counts on your

integrity. Please register using the form at the end of this

manual, or the form included in the file "ELECTRC7.REG".

Registration entitles you to an expanded, 'Registered-User'

version of this program. See the end of this manual for details.

I

*  DISCLAIMER OF WARRANTY  *

|

| THIS SOFTWARE AND DOCUMENT ARE OFFERED "AS IS" AND WITHOUT

| WARRANTIES AS TO PERFORMANCE OF MERCHANTABILITY OR ANY OTHER

| WARRANTIES WHETHER EXPRESSED OR IMPLIED. BECAUSE OF THE VARIOUS

| HARDWARE AND SOFTWARE ENVIRONMENTS INTO WHICH THIS PROGRAM MAY

| BE PUT, NO WARRANTY OF FITNESS FOR A PARTICULAR PURPOSE IS

| OFFERED.

|

| GOOD DATA PROCESSING PROCEDURE DICTATES THAT ANY PROGRAM BE

| THOROUGHLY TESTED BEFORE RELYING ON IT. THE USER MUST ASSUME

| THE ENTIRE RISK OF USING THIS PROGRAM. THE AUTHOR OF THIS

| PROGRAM ASSUMES NO LIABILITY.

|

| DUE TO THE NATURE OF THIS PROGRAM, THE USER MUST BE FAMILIAR

| WITH THE SAFETY CONSIDERATIONS OF DESIGNING AND SAFELY

| INSTALLING ELECTRICAL WIRING SYSTEMS, IN ACCORDANCE WITH THE

| NATIONAL ELECTRICAL CODE. THIS PROGRAM IS NOT INTENDED TO

| REPLACE THE NEED FOR A QUALIFIED PERSON WHO IS EXPERIENCED IN

| THE ELECTRICAL DESIGN, CONSTRUCTION AND MAINTENANCE OF SAID

| ELECTRICAL SYSTEMS IN THEIR ENTIRETY.

|

|

|

|

|

|

| FILES ON ELECTRC7 DISK :

| -------------------------------------------------------

| Electrc7.reg          Registration Form

| Electrc7.doc          This documentation file

| Electrc7.exe          Electrc7 program

| Electrc7.bug          Problem report form

| Conduit.dat           Data file of conduit prices

| Fittings.dat          Data file of fittings prices

| Wire.dat              Data file of wire prices

|

|

|

|

|

|

|

| The importance of making a working copy of this, or any other

| program disk cannot be too strongly stressed ! Please STOP NOW

| and copy all the files included on the ELECTRC7 disk to a

| blank formatted disk, and place the original in a secure place.

II

Introduction:

-------------

ELECTRC7 is designed to perform most common electrical contracting

and engineering calculations :

* Device, junction and pull box calcs.

* Conduit size selection for many combinations of different wire

sizes & types.

* Power/voltage/current/resistance of resistive loads.

* Determine the cost to operate various loads at different

kwh charges.

* Lighting calculations based on zonal cavity method.

* Motor conductor, overcurrent and overload calculations.

* Calculate required wire and conduit size based on allowable

voltage drop.

* Pipe and Wire Cost Comparator with user modifyable price lists.

* Quick reference tables for:

Grounding electrode conductor size,

Equipment grounding conductor size,

Underground cover requirements, and

KW to ampere conversion tables.

* Calculate voltage drop for various loads, voltages, wire size

and run lengths.

** All functions in this version conform to the 1987 National

Electrical Code. "Registered-User" version conformance is

available for either the 1987 or the new 1990 Code. See the

'Registration' section at the end of this manual for further

information.

Page 1

DEVICE BOX FILL CALCULATIONS:

----------------------------

Determines cubic inch volume required for boxes, (including

extension rings, raised covers, etc.) as per NEC section 370-6.

Conductor size range is from #18 thru #6. Deductions for fittings,

devices, etc. are based on free space required for the largest

conductor entering the box.

Free space (cubic in.) required for each conductor is as follows:

----------------------------------------

# 18 .. 1.5                  # 10 .. 2.5

# 16 .. 1.75                 # 8 ... 3

# 14 .. 2                    # 6 ... 5

# 12 .. 2.25

Deductions are as follows:

-------------------------

1 or more Fixture studs, cable clamps, hickeys  1 deduction

Each Strap containing 1 or more devices ....... 1 deduction

1 or more grounding conductors entering box ... 1 deduction

1 or more Isolated Ground conductors .......... 1 deduction

A list of wire sizes from #18 thru #6 will be shown. Then a

hilighted prompt will be positioned adjacent to the # 18 wire

size. Enter the quantity of #18 conductors and press ENTER to

record that quantity and to advance the prompt to the next

conductor size. If there are no #18 conductors, then just press

ENTER. The prompt will advance to the next conductor size.

Follow this procedure through the last conductor size (#6). You

may enter any combination of conductor sizes.

Next you will be asked for the quantity of device straps, if there

are any fittings, grounding conductors, or isolated ground

conductors entering the box. Simply answer each prompt in

succession, pressing the ENTER key to advance.

After the last prompt is answered, the results will be displayed.

A quick reference table of standard metal boxes and their cubic

inch capacity is available for viewing. It can be selected at this

point by pressing the SPACEBAR. The current screen will be saved,

and the table will be shown. When you wish to return to the

previous screen, press any key. This may be repeated if you wish.

Page 2

JUNCTION, PULL BOX CALCULATIONS:

Straight Pull:

-------------

Calculates the minimum length, in inches, of pull and junction

boxes where raceways enter and leave the box at opposite ends. If

the wiring method is cable assemblies instead of raceways, first

determine the trade size conduit which would be appropriate for

the size and quantity of conductors in the cable assembly, then

use that conduit size.

If more than one raceway or cable enters and/or leaves either end

of the box, always use the largest size.

The method used to determine minimum box length for straight pull:

Eight times the trade diameter of the largest raceway.

The operation of this function is straightforward. Position the

hilighted bar over the largest raceway size for this calculation,

then press ENTER. The results will be displayed.

Angle or U Pull:

---------------

Calculates the minimum distance, in inches, between each raceway

entry inside a junction or pull box and the opposite wall of the

box, where raceways enter and leave the box at right angles. If

the wiring method is cable assemblies, see the explanation above,

under 'Straight Pull'.

The method used to determine minimum distance for angle or U Pull:

Six times the trade diameter of the largest raceway, PLUS,

the sum of the diameters of all other raceway entries in any one

row on the same wall of the box. Use the row with the largest

total diameter of raceways.

Enter the quantity of the conduit size that the hilighted prompt

is adjacent to, then press ENTER to record that quantity and

advance to the next size. Just press ENTER to record none and

advance to the next size.

View Metal Box Table:

--------------------

A quick reference table of standard metal boxes and their cubic

inch capacity is available for viewing. It can be selected from

the 'Junction, Pull Box Calculations' sub menu or after executing

the 'Device Box Fill Calculations' function.

Page 3

CONDUIT SIZE SELECTOR:

---------------------

Calculates the trade size of conduit required for a group of

conductors.

The Conduit Size Selector allows you to quickly and accurately

determine the conduit size required for 1 or more conductors.

Calculations are based on the Dimensions and Percent Area of

Conduit and Tubing from table 4 of the NEC. Maximum allowable

percent conduit fill is 53% for 1 conductor, 31% for 2

conductors and 40% for more than 2 conductors, as per table 4.

Use the UP, DOWN, LEFT or RIGHT arrow keys to move the cursor

block to the desired wire size/type position, then enter the

quantity of that size/type to include in the conduit. At this

point you can press ENTER to record that entry or you can abort

that entry by moving the cursor block with the direction keys.

You can use the BACKSPACE key to edit the entry at any time. If

you want to include other size/types of conductors into the same

conduit, then repeat the above procedure. You can enter any

combination of conductors in the same conduit. When you are

finished entering, press the CONTROL and END keys together. The

program will then list all the conductors you chose for the

calculation, and calculate and display the required trade size

conduit required. Pressing the ESCAPE key at any time will abort

to the main menu.

GENERAL CALCULATIONS

Cost to Operate:

---------------

Calculates the cost to operate a certain load a number of hours

daily for some number of days at a certain KWH utility charge.

POWER OF LOAD is the number of WATTS the load draws.

DAILY USE is the number of HOURS the load is operated per day.

NUMBER OF DAYS is the number of days in the billing period.

PRICE / KWH is the utility charge per killowatt hour.

(Example..  9 cents/kwh, enter .09)

Enter the value at the hilighted prompt for each parameter, then

press ENTER to record that value and advance to the next

parameter.

After entering the above information, the program calculates and

displays the dollar cost to operate the load for the number of

hours daily for the number of days at the chosen utility charge.

Page 4

Ohm's Law Calcs:

---------------

Calculates values for two unknown values of power, voltage,

current or resistance in DC circuits or in purely resistive AC

circuits.

If you want to solve for Power, Voltage, Current or Resistance,

you only need to know 2 of the 4 values.

Enter the value and press ENTER at the prompt for each of the two

known parameters. If the prompt is adjacent to an unknown

parameter, just press ENTER.

As soon as any two parameters have been entered with values other

than zero, the results are calculated for the remaining two, and

are displayed.

LIGHTING CALCULATION ( Zonal Cavity Method ):

--------------------------------------------

Calculates the quantity of lighting fixtures required to light any

room or area to any desired footcandle level.

The Illuminating Engineering Society (IES) has devised a flexible

and accurate method for calculating lighting requirements, called

the ZONAL CAVITY METHOD. This method assumes that any room or area

to be lighted is made up of three cavities, the CEILING CAVITY,

the ROOM CAVITY, and the FLOOR CAVITY.

The CEILING CAVITY extends from the ceiling surface down to the

lighting fixture mounting level. If the lighting fixtures are

recessed or surface mounted then the value of the Ceiling Cavity

will be zero. If they are suspended some distance below the

ceiling then the value of the Ceiling Cavity is the volume of

space between the ceiling surface and the fixture mounting level.

The ROOM CAVITY extends from the fixture mounting level down to

the work height level. The work height level is the distance above

the floor where the required quantity of footcandles is to be

maintained (usually desktop or work bench top level).

The FLOOR CAVITY extends from the work height level down to the

floor. If the required footcandles is to be maintained all the way

to the floor, then the Floor Cavity value will be zero. Every

surface exibits a certain ability to reflect light. Light colored

surfaces reflect more light than dark surfaces, so more light will

need to be provided in a dark environment. The degree of a

surface's reflectivity is referred to as it's Percent Reflection

value. Percent Reflection can be accurately measured with a

reflectometer, or standard reflectance tables can be referred to,

such as the following:

Page 5

TABLE FOR INTERIOR ILLUMINATION DESIGN

----------------------------------------

COLOR                % REFLECTION

----------------------------------------

Flat white               75 - 85

Ivory                    70 - 75

Buff                     60 - 70

Yellow                   55 - 65

Light tan                45 - 55

Light green              40 - 50

Gray                     30 - 50

Blue                     25 - 35

Red                      15 - 20

Dark brown               10 - 15

------------------------------------------

The MAINTENANCE FACTOR is a value determined from the anticipated

maintenance of the fixtures and reflective surfaces in the room or

area. The intensity of illumination produced by a lighting

installation will depreciate after some time due to lamp aging,

and dust and dirt buildup. The MAINTENANCE FACTOR is designed to

adjust for this. Typical values are from .5 to .8. (.5 for a

poorly maintained environment, .8 for well maintained). Each

lighting equipment manufacturer publishes data for the COEFFICIENT

OF UTILIZATION (CU) for each fixture type and size in it's line.

The CU of a fixture is a measure of it's efficiency under specific

conditions of room cavity values and effective reflectance values.

The formulas used in the ZONAL CAVITY METHOD :

CEILING CAVITY RATIO = (5 * Hc (L + W)) / (L * W)

ROOM CAVITY RATIO =  (5 * Hr (L + W)) / (L * W)

FLOOR CAVITY RATIO = (5 * Hf (L + W) / (L *  W)

WHERE:

Hc = distance from ceiling to fixture level (in feet).

Hr = distance from fixture level to work height (in feet).

Hf = distance from work height to floor (in feet).

L = length of room in feet.

W = width of room in feet.

Page 6

PROGRAM USAGE:

ROOM LENGTH and ROOM WIDTH values must be entered in FEET.

Decimal points are accepted (Ex. 125, 50.5, etc...) The Maximum

acceptible value for each input is 1000.

CEILING HEIGHT and FIXTURE HEIGHT must also be entered in FEET.

Decimal points are acceptable.

WORK HEIGHT must also be entered in FEET. Decimal points are

acceptable. If you want the WORK HEIGHT to be equal to the

floor, simply press the ENTER key at that prompt, or enter zero.

Values for CEILING, WALL, and FLOOR REFLECT must be entered as

whole numbers (50, 80, etc...) Exact values can be obtained by

use of a reflectometer, or a standard table for interior

illumination design can be referred to, such as the table for

interior illumination design on the previous page.

The value entered for MAINT. FACTOR must be less than or equal to

1. The value of between .5 and .8 will be accurate for nearly all

calculations. A value of 1 will exclude the MAINTENANCE FACTOR

from the lighting calculation.

After the above values have been entered, a second box will appear

and internally calculated values will be displayed within the box.

After all calculations and displays are completed in the second

box, a third box will appear. You will be presented with a Fixture

Type Menu. From here you can choose fixture types contained

internally or you can choose to specify your own fixture. Fixture

types stored internally include Recessed Incandescent,

Fluorescent, and High Intensity Discharge. COEFFICIENT of

UTILIZATION values which have been compiled by IES are stored

internally for these fixtures. The internally stored fixtures are

representitive of their types. You will get accurate results using

them, but if you wish to use a type of fixture not available

internally, you can choose to specify your own type.

If you choose 'SPECIFY', you will be prompted for the CU of your

fixture. You will need to have the fixture manufacturer's CU

specs. Next you will be prompted for the number of LAMPS per

fixture and for the LUMENS per lamp. LUMEN specs are available

from various sources. Your electrical supply house generally has

lamp catalogs from General Electric and other lamp manufacturers

which will list LUMEN values for their line.

After the fixture type (INTERNAL or SPECIFY) has been selected and

the prompts have been answered, the program will calculate the

required quantity of fixtures and display the result on screen.

From here you can choose to recalculate using a different fixture

type, lamp size, etc., for the previously entered room data. A

sort of 'what-if' calculation, without having to re-enter all the

room data. To do this, just press the ENTER key.

Page 7

MOTOR CALCULATIONS - Single Phase

This version supports single phase motors only. The 'Registered-

user' version also supports three phase motors, plus additional

functions. See the 'Registration' section at the end of this

manual for further information.

Branch Conductor Sizing:

-----------------------

Calculates motor branch circuit conductor size.

Conductor ampacity is based on 125 percent of motor full load

amperage, as determined from NEC table 430-148.

Selects proper size conductor for types THW and THHN Copper.

Fuse or Breaker Sizing:

----------------------

Calculates maximum rating or setting of motor branch circuit

overcurrent protection device (Nontime-delay fuse, Time delay

fuse, Instantaneous trip cct breaker & Inverse time cct breaker).

Rating or setting is based on Full load amperage (from table 430-

148) of motor, multiplied by appropriate percentage factor from

table 430-152 for the selected device type. If this results in a

value other than a standard size or rating of overcurrent

protection device, the next higher standard rating is also

displayed.

Overload Protection Sizing:

--------------------------

Calculates maximum motor overload protective device rating.

Rating is based on motor full load amperage (from motor nameplate)

multiplied by:

125 % if marked service factor is not less than 1.15, or

125 % if marked temperature rise is not over 40 degrees C., or

115 % for all others.

Page 8

PIPE & WIRE SELECTOR and COSTCOMP:

---------------------------------

Calculates the conductor size required to carry a certain load for

some distance at a certain voltage while not exceeding a specific

voltage drop percentage. Types THW and THHN, copper and aluminum

are supported. Ambient temperature derating as per NEC is

supported. Power Factor is assumed to be 100%. If it is other than

100%, then first calculate the load current including the power

factor, then use the new load amperage for accurate results.

Also selects the correct size raceway for the conductors and shows

the difference in cost of using type THN conductors and type THHN

conductors. Sometimes a lower total installation cost can be

achieved by using type THHN conductors instead of type THW because

a smaller raceway may be used. This function will display the

individual costs of the required conductors, raceway and fittings

and the total installation cost for the use of THW and THHN

conductors. EMT, PVC and Galvanized Rigid conduits are supported,

as well as their associated connectors, couplings and sweeps.

The prices for the raceways and fittings are in the three included

files - Conduit.dat, fittings.dat and wire.dat. The prices may be

changed at any time from within the program. See the 'Modify

Database Prices' documentation in this manual.

This function asks for values of Maximum allowable voltage drop

percentage, conductor material, load amperage, source voltage,

circuit length, circuit type, and the ambient temperature.

After you have entered the requested information, the program will

calculate the required conductor size for both THW and THHN. You

may then choose a COST COMPARISON by pressing and holding the

CONTROL key and pressing the END key. A new input screen will

appear and you will be prompted for the raceway type that you

choose to use. The types presently supported are "E.M.T.",

"P.V.C." and "Galvanized Rigid". Choose the type that you wish to

use. Next you are prompted for the quantity of "PRE-BENT SWEEPS".

Enter the quantity you need to use, then press the ENTER key. If

you will not be using any, simply press the ENTER key. Next enter

the quantity of "CONNECTORS", and then the quantity of

"COUPLINGS". If you need none, simply press the ENTER key. The

data files FITTINGS.DAT, WIRE.DAT and CONDUIT.DAT will be accessed

and searched for the appropriate materials and unit prices. The

program will then display the list of materials and end prices for

the selected materials, then the total material cost for both the

THW materials and the THHN materials.

Page 9

DESIRED % VOLTAGE DROP is the maximum allowable for that

calculation. Do not enter the percent sign (%).

Example: For desired max. volt drop of 3%, enter 3

COPPER or ALUMINUM is self explanatory.

AMPERAGE OF LOAD is the amperage required by the load.

SOURCE VOLTAGE is the voltage measured at the source of power.

LENGTH OF RUN is the distance in FEET from the source of power

to the load terminals.

TYPES OF CIRCUITS:

1.   Single Phase - Phase and neutral or 2 Wire Single Phase

( Example... 120, 277) or (208, 240)

2.   3 Phase 3 Wire - Three Phase, no neutral

( Example... 208, 240, 480)

3.   3 Phase 4 Wire - Three phase & neutral

( Example... 120/208, 277/480)

4.   Single Phase 3 Wire - Two phases & neutral

(from a 3 phase 4 wire Y system)

If you choose circuit type 3, you will be asked if the major

portion of the load will consist of electric discharge lighting,

data processing or similar equipment. These loads typically result

in harmonic currents being present in the neutral conductor.

Therefore the circuit will consist of 4 current carrying

conductors in the raceway or cable, and the ampacity must be

derated as per NEC note 8 to tables 310-16, in addition to any

other required derating factors. At the prompt, enter Y or N.

AMBIENT TEMPERATURE: An input menu allows you to enter the ambient

temperature which surrounds the conductors. Use the UP ARROW and

DOWN ARROW keys to place the hilighted selection bar over the

temperature range of your choice, then press the ENTER key to

accept that choice. Temperature ranges are displayed in both

Centigrade and Fahrenheit. The first (uppermost) displayed menu

choice, "Do Not Derate", is based on an ambient temperature of 30

deg/c., and so no derating factor need be applied at that

temperature. If you choose an ambient temperature of 71-80 deg/c

(159-176 deg/f), type THW will not be calculated because it's

temperature rating is exceeded at that temperature. Type THHN will

be displayed, though.

After entering values for the above parameters, the program will

calculate and display the correct conductor size required for

types THW and THHN.

Page 10

EQUIPMENT GROUND CONDUCTOR TABLE:

--------------------------------

To determine the required size equipment ground conductor,

as per NEC Table 250-95.

GROUNDING ELECTRODE CONDUCTOR TABLE:

-----------------------------------

To determine the proper grounding electrode conductor size,

as per NEC Table 250-94.

KW TO AMPERE TABLES:

-------------------

To quickly convert single and three phase KW values to ampere

values and vice versa. Pressing the SPACEBAR scrolls between the

single phase and three phase tables.

UNDERGROUND COVER TABLE:

-----------------------

To determine the minimum cover requirements of conduit,

underground cable, and other raceways, as per NEC Table 300-5.

SETUP - COLOR AND DATABASE PRICES

Color Defaults:

--------------

As supplied, the program starts up in black and white. Select

'Color Defaults' from the Setup submenu, and you can press the

SPACEBAR to scroll through all available screen colors. When you

have reached the desired color combination, press the ENTER key.

The chosen colors will be saved to disk, and thereafter the

program will start up with those colors, until you change them.

Page 11

Modify Database Prices:

----------------------

To change the material prices in the supplied data files. The data

files can be modified to reflect whatever prices you wish.

The three data files are:

CONDUIT.DAT ................ Raceway prices.

WIRE.DAT ................... Conductor prices.

FITTINGS.DAT ............... Fitting prices.

All 3 files must be in the same drive and directory as the

ELECTRC7 program file.

A selection menu will allow you to choose the data file(s) to

modify. Use the UP or DOWN ARROW keys to place the highlighted

selection bar over the price file of your choice, then press the

ENTER key to select that choice. If a required data file is not

found on the disk, you will be alerted, and returned to the menu.

A key action list will be displayed, describing the available

editing functions. The file will be opened and the first item in

that file will be displayed. A highlighted bar is placed over the

current price for that particular item. You may enter a new price

for that item, or you may browse through all the items in that

file, without changing any of the current prices. When you are

finished with that file, pressing the ESCAPE key will save the

changes and return you to the Modify sub-menu, where you can

select another file, or quit to the main menu.

VOLTAGE DROP CALCULATOR:

-----------------------

Calculates the voltage drop on existing or proposed single phase

or three phase AC circuits. Copper and aluminum conductors from

#14 to 2000 mcm are supported.

The Voltage Drop Calculator asks whether or not the load is single

phase, the length of the run, the source voltage, the load

amperage, and the wire conductor size and material. The resultant

calculation is based on the Ohms/mil/ft of the specified conductor

size and material, the circuit length, and the load amperage

At the prompt " Is load Single Phase ?", if you answer no it is

assumed to be three phase.

The RUN LENGTH is the length in feet from the source of power

to the load terminals.

The SOURCE VOLTAGE is the voltage measured at the source of

power.

Page 12

The AMPERAGE is the current required by the load. For example,

if the load is a resistance heater requiring 10 amps to operate

as designed, then the AMPERAGE would be entered as 10.

The WIRE SIZE is in the range of #14 awg to 2000 mcm. Do not

include the # sign or the letters mcm. At the prompt, enter the

numeric size of the wire (ex. 14, 1/0, 250, 750).

The COPPER or ALUMINUM prompt is self explanatory.

After entering the above values, the program will calculate and

display:

1. The VOLTAGE DROP of the circuit (the number of volts dropped).

2. The VOLTS AT LOAD (the voltage delivered to the load terminals)

3. The % DROP (the percentage of the source voltage dropped)

Page 13

================================================================

REGISTRATION

----------------------------------------------------------------

When you register your copy of Electrc7, an expanded 'Registered

User' version of the software will be shipped to you immediately.

That version will support these additional functions:

* Three phase motor calculations:

Branch conductor sizing,

Overcurrent protection sizing, and

Overload protection sizing.

* Horsepower ratings not available in this version.

* Motor types not available in this version.

* Motor starting methods not available in this version.

* Additional general calculations - Single & 3 Phase:

Amperes when motor HP, PF and EFF. is known,

Amperes when watts or VA and PF is known,

Watts or VA when voltage, current and PF is known,

Motor HP when voltage, current, efficiency and PF are known.

* Additional quick reference tables:

Transformer KVA and Ampere ratings - Single and 3 Phase,

Standard fuse and breaker size ratings,

Standard pull and junction box sizes with respective volumes,

* Elimination of the program's opening screen.

Two 'Registered-User' vrsions are available. One based on the 1987

NEC and one based on the new 1990 NEC. The registration fee for

either version alone is 35.00 and for both versions is 45.00. Be

sure to specify which version(s) you need on the registration

form. Each version is shipped on an individual disk.

Page 14

ELECTRC7 Copyright 1989, Robert J. La Capra

==  REGISTRATION FORM  ==

Name: _______________________________________________________

Company: ____________________________________________________

Address: ____________________________________________________

City,State,Zip:______________________________________________

Which Version(s):    [ ] 1987       [ ] 1990       [ ] Both

Fee Enclosed: $__________

Where did you obtain ELECTRC7 ?:

_____________________________________________________________

Suggestions & Comments, if you wish:

_____________________________________________________________

_____________________________________________________________

_____________________________________________________________

_____________________________________________________________

_____________________________________________________________

_____________________________________________________________

_____________________________________________________________

==================================================================

Two 'Registered-User' vrsions are available. One based on the 1987

NEC and one based on the new 1990 NEC. The registration fee for

either version alone is 35.00 and for both versions is 45.00. Be

sure to specify which version(s) you need on the registration

form. Each version is shipped on an individual disk.

Send this form and registration fee to:

Robert J. La Capra

50 Hillside Terrace

Andover, NJ 07821

Once again, thanks for using and supporting ELECTRC7. As always,

any questions, comments and suggestion are welcome.

==================================================================

Page 15