|

|

|

|

|

|

|

|

|

|

|

|

|        ELECTRC9

|

|        Copyright 1992, by Robert J. La Capra

|        All Rights Reserved

|

|        Shareware Version 9.2

|

|

|

|

|

|

|

|

|

|        USER'S MANUAL

|

|

|

|

|

|

|

|

|

|        Robert J. La Capra

|        50 Hillside Terrace

|        Andover, NJ 07821

|

|

|

|

|

|

|

|

|

|

|

|

|

|

TABLE OF CONTENTS

Introduction .............................................. I

Shareware ................................................ II

Benefits Of Registration ................................. II

How To Register .......................................... II

Functions Supported By Registered User Version .......... III

Product Support Policy ................................... VI

ELECTRC9 Registration Form .............................. VII

Disclaimer ............................................. VIII

Files Included On ELECTRC9 Disk ........................ VIII

SETTING UP ELECTRC9

Making A Backup Copy Of The ELECTRC9 Disk ........... IX

Setting Up ELECTRC9 On A Floppy Disk ................ IX

Setting Up ELECTRC9 On A Hard Drive ................. IX

RUNNING ELECTRC9

From A Floppy Disk ................................... 1

From A Hard Drive .................................... 1

Menu Selection ....................................... 1

Data Input ........................................... 1

Selecting Conductors ................................. 2

Setup Color Defaults ................................. 2

BOX FILL & SIZING CALCULATIONS

Device Box Fill & Sizing ............................. 2

Junction, Pull Box Sizing - Straight Pull ............ 4

Junction, Pull Box Sizing - Angle or U Pull .......... 4

CONDUIT SELECTOR .......................................... 5

GENERAL CALCS:

Cost To Operate ...................................... 6

Motor Amps When Hp, Pf, And Efficiency Are Known ..... 6

Motor Hp When Volts, Amps, Pf And Efficiency Are Known 7

Amps When Va And Pf Are Known ........................ 7

Va When Volts, Amps, And Pf Are Known ................ 7

LIGHTING CALCULATIONS (Zonal Cavity Method) ............... 8

MOTOR CALCULATIONS

Branch Conductor Sizing ............................. 11

Fuse or Breaker Sizing .............................. 11

Overload Protection Sizing .......................... 12

PIPE & WIRE SELECTOR ..................................... 13

POWER FACTOR CORRECTION .................................. 14

PRINTING REPORTS ......................................... 16

QUICK REFERENCE TABLES

Equipment Grounding Conductors ...................... 16

Grounding Electrode Conductors ...................... 16

Killowatt - Ampere Tables ........................... 17

Underground Cover Requirements ...................... 17

Metal Device Boxes .................................. 17

Standard Pull & Junction Boxes ...................... 17

Standard Fuses & Breakers ........................... 17

Transformer Kva - Amperes ........................... 17

Terminal/Conductor Temperature Limitations .......... 17

Conductor Ampacity .................................. 18

SHORT CIRCUIT CALCS ...................................... 18

TERMINAL/CONDUCTOR TEMPERATURE LIMITATIONS ............... 22

VOLTAGE DROP CALCULATOR .................................. 23

OTHER ELECTRICAL SOFTWARE AVAILABLE

LOADCALC Service/Feeder Calcs Version 1.1 ........... 24

NOTE !!

Pages 1 thru 23 of this file includes all documentation text

from the Registered User Version of ELECTRC9. However, not

all referenced features are available in this Shareware

Version of the program. The full text is included here to

give you a better idea of what the Registered User Version

supports.

__________________________  Page I  _________________________

INTRODUCTION

This Shareware evaluation Version Of ELECTRC9 is designed to

perform most common electrical contracting and engineering

calculations :

* Device, junction and pull box calcs.

* Conduit fill calculations.

* Cost to operate various loads at different kwh charges.

* Lighting calculations based on the Zonal Cavity Method.

* Motor conductor, overcurrent and overload calculations.

* Wire and conduit sizing based on allowable voltage drop.

* General Calculations:

Amps when hp, pf, and efficiency are known

Amps when va and pf are known

Va when volts, amps, and pf are known

Hp when volts, amps, pf and efficiency are known

* Quick Reference Tables for:

Grounding electrode & equipment ground conductor sizes

Underground cover requirements

KW to ampere tables

Transformer Kva to ampere tables

Device, pull & junction box size and capacity

Standard fuse & breaker ratings

Wire ampacity table

New terminal temp rating requirements - NEC 110-14(c)

* Voltage drop calcs.

* Power factor correction.

* All functions operate with 'what-if' capability. You can

quickly and easily change only the data you wish to,

without having to start a new calculation and re-enter all

the required data. Results are calculated and displayed as

you make each change.

** All functions conform to the 1993 National Electrical Code.

The National Electrical Code is a copyrighted document of the

National Fire Protection Association, Batterymarch Park,

Quincy, MA. 02269.

__________________________  Page II  ________________________

SHAREWARE

ELECTRC9 is copyrighted (c) 1992, By Robert J. La Capra.

ELECTRC9 is not free software. This shareware version is made

publicly available only to allow users to preview ELECTRC9 on

a trial basis. Any use of this shareware version beyond this

limited evaluation period requires registration with the

author, as described below. Use of unregistered copies past

the evaluation period is prohibited.

BENEFITS OF REGISTRATION

Registration of ELECTRC9 brings you the following benefits:

You receive the latest, expanded 'Registered User' version of

ELECTRC9, which supports functions and capabilities in

addition to those supported in this shareware version. The

Registered User Version will not have the opening or closing

shareware screens.

You support the 'Shareware' concept of marketing which allows

you to try the software before making a purchase.

You receive unlimited priority support by US Mail, CompuServe

Mail, and optional fax support.

You receive automatic notification of future upgrades and new

programs as soon as they become available. These are also

offered to you at substantial discounts.

Read the 'Product Support Policy' in this file for the major

benefits of becoming a Registered User, and the 'Functions

Supported By Registered User Version', in this file.

HOW TO REGISTER

A single registration of ELECTRC9 may be used by only one

user at a time - it may not be installed on a server,

network, etc..., nor may it be copied for use on multiple

machines at one time, or be potentially available for use by

more than one person at a time. A Single User Licensing

Agreement will be supplied for each user that you register.

To encourage ethical use of ELECTRC9, discounts are available

for multiple registrations. Available licensing agreements

range from six or more users to unlimited site licenses, in

several increments. Write for current availability & fees.

To register, fill out completely and mail the ELECTRC9

Registration Form included in this file, or the one supplied

in the disk file "ELECTRC9.REG", with the appropriate fee.

_________________________  Page III  ________________________

FUNCTIONS SUPPORTED BY THE REGISTERED USER VERSION

Conduit Fill & Sizing

Selects raceway size for any combination of insulated

conductors. Calculates individual & total conductor areas,

total area of raceway selected, and percent conduit fill. #18

thru 2000 kcmil copper & aluminum conductors. Types tw, thw,

thwn, thhn, rhw, rhh, use, xhhw.

Power Factor

Determines existing PF based on measured line volts, line

amperes and true power you supply. Calculates Kvars needed to

raise existing PF to any new PF. Specifies phase angle, Kva &

Kvar of existing and proposed PF. Specifies recovered

distribution system losses at the proposed PF. Single phase

and balanced three phase.

Box Fill & Sizing

Calculates minimum cubic inch capacity of device boxes based

on intended conductor/device/fitting fill. Selects minimum

box dimensions for straight and angle pull and junction boxes

Pop-up quick reference tables for standard dimensions and

cubic capacities of device, junction & pull boxes are

viewable with a single keypress.

Lighting Design

Performs interior lighting design based on the Illuminating

Engineering Society's Zonal Cavity Method. Calculates

required fixture quantity for any desired footcandle level.

Supports cavity ratios, surface reflectances, and maintenance

factors. Built-in support for generic recessed incandescent,

fluorescent and hid fixtures as well as many lamp types. Also

allows you to specify any fixture/lamp combination with data

you can obtain from the manufacturer of the fixture/lamp that

you choose to specify.

Pipe & Wire Sizing

Selects conductor size for any load amperage and picks

correct raceway size for those conductors. Supports 6 circuit

types, including harmonic. 21 supported conductor

material/insulation/temperature rating combinations. Derating

for ambient temperature & for the number of current carrying

conductors contained in the raceway. Terminal temperature

limitations. You can also choose to specify a maximum voltage

drop percentage which cannot be exceeded, and supply the

circuit run length, and the correct conductor will be

selected Supports single & three phase.

_________________________  Page IV  ________________________

Motor Calcs

Selects motor branch circuit conductors. Selects overcurrent

protective device ratings. Selects motor overload protection

ratings. Supports squirrel cage & wound rotor motors.

Supports full voltage, resistor, reactor & autotransformer

starting methods. Supports 21 conductor

material/insulation/temperature rating combinations. Supports

all code letters. Ambient temperature derating. Terminal

temperature limitations. Time delay & non time-delay fuses.

Instantaneous trip & inverse time circuit breakers. 110-240

volt, .17-10 HP Single Phase. 208-480 volt, .5-200 HP Three

Phase.

Voltage Drop

Calculates voltage drop on existing or proposed resistive

circuits (100% PF) at any voltage, amperage and run length.

Supports circuit conductors from #18 awg thru 2000 kcmil,

aluminum & copper. Displays volts dropped, volts at load

terminals and the percentage of voltage dropped. Single &

three phase.

Short Circuit

Calculates available fault currents from the source to a

maximum of 10 downstream points on the distribution system.

Calculations include the effect of voltage drop, impedance

and the inductive effects of the conductor/raceway system.

Supports single & parallel conductor runs, #12 awg thru 1000

kcmil, copper & aluminum. Supports magnetic & non-magnetic

raceways. Single & three phase.

General Calcs

Calculates the cost to operate any load for any number of

hours per day for any number of days at any utility Kwh rate.

Calculate motor amps when hp, pf, & efficiency are known.

Calculates motor hp when volts, amps, pf & efficiency are

known. Calculates amps when va, volts & pf are known.

Calculates va when volts, amps & pf are known.

_________________________  Page V  _________________________

Quick Reference

Built in reference table screens that can be accessed from

the main menu, and from within certain functions for which

they are in context. They can be viewed on screen and can be

printed to printer or disk file. Conductor ampacities,

temperature ratings & ambient correction factors as per NEC

Table 310-16. Terminal temperature limitations as per NEC

110-14(c). Kw to amperes. Transformer Kva to amperes.

Underground cover requirements as per NEC 300-5. Standard

pull & junction box dimensions and cubic capacities. Standard

metal device box dimensions and cubic capacities as per NEC

370-16(a). Grounding electrode sizing as per NEC 250-94.

Equipment grounding conductor sizing as per NEC 250-95.

Standard fuse & circuit breaker ratings. Three phase tables,

where appropriate.

Printed Reports

Professional, detailed reports for all program functions.

Send reports out to a printer, or to an ASCII disk file where

you can then import the report into your word processor and

fine tune the appearance before printing. You can input up to

four lines of data which will print at the top of your

report. Printer output is generic, will work on any printer

connected to parallel port LPT1.

What-If Data Input

Quickly and easily see what effect a change of one data item

will have on the result of the design you are working on.

Once you have entered all required data within a function and

the function has calculated the result, you can then change

one data item at a time and the function will automatically

recalculate the results instantly. Great for quick

comparisons of alternate design specs.

NEC Compliance

ELECTRC9 has been written to produce design specifications

that comply with the 1993 National Electrical Code.

System Requirements

To run ELECTRC9, you will need to have the following minimum

hardware configuration: An IBM or compatible computer. Any

brand or version of DOS 2.11 or greater. 390 K of free memory

available. One floppy disk drive. Monochrome or color

monitor.

_________________________  Page VI  _________________________

PRODUCT SUPPORT POLICY

Your registration of ELECTRC9 software will entitle you to

extended product support services and other features which

are intended to provide you with continuous satisfaction.

The Registered User version of ELECTRC9 that you receive upon

registration will support many enhancements and capabilities

that are not available in this Shareware version.

If any program bugs are discovered which affect the intended

functionality or accuracy of the program, a revised program

will be sent to you, as a Registered User, free of charge.

As a Registered User, you will automatically be notified of

any upgrades and new programs as they become available.

Upgrades will be made available to you at reduced fees.

You, as a Registered User, will have unlimited free support

via US Mail. No phone support is presently available.

If you have access to the CompuServe Information Service,

you, as a Registered User, will also have unlimited priority

support via CompuServe Mail, by leaving me a Mail Message.

Your message will generally be answered within 24 hours or

less. No messages will be accepted or returned through any

gateways of other electronic mail services, or in any case

where postage is due.

If you select the optional fax support subscription for

ELECTRC9 when you register, you will have one year of

unlimited fax support for ELECTRC9. The fax number will be

included with your disk shipment.

Your feedback is the most important planning and development

tool available to me. I look forward to hearing your thoughts

about the present capabilities of the software, your wish

list for additions and modifications of future versions, and

any additional ideas for making the software more useful to

yourself and other users.

_________________________  Page VII _________________________

ELECTRC9 Ver. 9.2 REGISTRATION FORM

S1234

Registration fee for 1 to 5 users is $59.00 for each user or

machine. Site License & Multiple discounts available for 6 or

more users. Write for info. Purchase orders without payment

attached cannot be accepted. US funds drawn from a US bank.

INCLUDED WITH YOUR REGISTRATION

Latest program version and documentation file.

Documentation is supplied on disk file. No printed manuals.

One License To Use Software for each user registered.

Unlimited support by US Mail and by CompuServe Mail.

No phone support available.

Shipping via US Postal Service.

Orders shipped same day registration received.

OPTIONAL ITEMS

* UPS Ground Delivery - $10.00 additional per order. Multiple

registrations or registration of ELECTRC9 and LOADCALC

together qualify as 1 order, and shipping is $10.00 total.

Supply street address. NO P.O. BOXES.

* 1 Year Of Fax Support for ELECTRC9 - $10.00 additional per year.

For multiple registrations of ELECTRC9, fee is still $10.00

total. Fax # supplied with shipment.

Return This Form And Registration Fee PAYABLE TO:

ROBERT J. LA CAPRA

50 Hillside Terrace

Andover, NJ 07821

S.S.# 137-44-7561

SHIP TO:

Name: _______________________________________________________

Company: ____________________________________________________

Address: ____________________________________________________

City,State,Zip: _____________________________________________

Phone : ______-______-________    Fax : ______-______-_______

Number Of Users: ______ x $59.00 Each = Reg. Fee . : $_______

UPS Ground Shipping - $10.00 Per Order [Optional]  : $_______

1 Year Of ELECTRC9 Fax Support - $10.00 [Optional] : $_______

_____________________________________________________________

TOTAL FEE ENCLOSED .... : $_______

DISK SIZE PREFERRED:   [   ] 5 1/4"     [   ] 3 1/2"

_________________________  Page VIII  ______________________

DISCLAIMER OF WARRANTY

THIS SOFTWARE AND DOCUMENT ARE OFFERED "AS IS" AND WITHOUT

WARRANTIES AS TO PERFORMANCE OF MERCHANTABILITY OR ANY OTHER

WARRANTIES WHETHER EXPRESSED OR IMPLIED. BECAUSE OF THE

VARIOUS HARDWARE AND SOFTWARE ENVIRONMENTS INTO WHICH THIS

PROGRAM MAY BE PUT, NO WARRANTY OF FITNESS FOR A PARTICULAR

PURPOSE IS OFFERED.

GOOD DATA PROCESSING PROCEDURE DICTATES THAT ANY PROGRAM BE

THOROUGHLY TESTED BEFORE RELYING ON IT. THE USER MUST ASSUME

THE ENTIRE RISK OF USING THIS PROGRAM. THE AUTHOR OF THIS

PROGRAM ASSUMES NO LIABILITY FOR YOUR USE OF THIS PROGRAM.

DUE TO THE NATURE OF THIS PROGRAM, THE USER MUST BE FAMILIAR

WITH THE SAFETY CONSIDERATIONS OF DESIGNING AND SAFELY

INSTALLING ELECTRICAL WIRING SYSTEMS, IN ACCORDANCE WITH THE

NATIONAL ELECTRICAL CODE. THIS PROGRAM IS NOT INTENDED TO

REPLACE THE NEED FOR A QUALIFIED PERSON WHO IS EXPERIENCED IN

THE ELECTRICAL DESIGN, CONSTRUCTION AND MAINTENANCE OF SAID

ELECTRICAL SYSTEMS IN THEIR ENTIRETY.

FILES INCLUDED ON ELECTRC9 DISK

Electrc9.Doc ... This documentation file

Electrc9.Exe ... Electrc9 program file

Electrc9.Reg ... ELECTRC9 Registration Form

Descrip.Doc .... Shareware Version Description

_________________________  Page IX  ________________________

SETTING UP ELECTRC9

Making A Backup Copy Of The Electrc9 Disk

The importance of making a backup copy of this program disk

cannot be too strongly stressed ! Please STOP NOW and copy all

the files included on the ELECTRC9 disk to a blank formatted

disk, and place the original in a secure place.

Setting Up ELECTRC9 On A Floppy Disk

You can use the backup disk created above to run ELECTRC9.

Setting Up ELECTRC9 On A Hard Drive

1. Create a subdirectory on the hard drive to hold all the

ELECTRC9 files as follows:

A. Log onto the root directory of the hard drive - If drive

is C:, type "C:" then press ENTER. Then type "CD\" and

press ENTER. (do not type the quotes).

B. Type "MD ELECTRC9" then press ENTER (you can substitute

any name for ELECTRC9 - do not type quotes).

2. Install the backup ELECTRC9 disk in floppy drive A: or B:

3. Log onto the floppy drive containing the backup disk -

(type "A:" or "B:" then press ENTER (do not type quotes).

4. Type "COPY *.* C:\ELECTRC9" then press ENTER (don't type

the quotes).

The installation is complete. To verify the setup went OK,

type "DIR C:\ELECTRC9\*.*" then press ENTER (no quotes). you

should see a directory listing showing the names of all the

files included on the ELECTRC9 disk.

_________________________  Page 1  __________________________

RUNNING ELECTRC9

From Floppy Disk

Insert the backup program disk into the disk drive and at the

DOS prompt type "ELECTRC9" then press ENTER.

From Hard Drive

Enter the directory where the ELECTRC9 files are located, and

at the DOS prompt type "ELECTRC9" then press ENTER.

SHAREWARE VERSION ONLY - In the shareware version of ELECTRC9,

you will first be asked to input a random number before you

are given control of the main menu.

Menu Selection

The main menu is a pull down type, structured as a horizontal

bar at the top of the screen with main titles displayed. Each

of these main titles represents a sub menu with one or more

related program functions.

To select specific program functions :

1. Press the hilighted letter of the menu item (main or sub).

OR,

2. Press the DOWN ARROW key to open the first sub menu, then

use LEFT or RIGHT ARROW keys to move between sub menus.

OR,

3. Position the hilighted block over a menu selection (main or

sub), then press ENTER.

Data Input

All functions operate with 'What-If' data entry routines. This

allows you to instantly see the results of changing one data

item at a time.

Data input routines are similar in all functions. Use the UP,

DOWN, or ENTER keys to move between input fields, entering

data as you go. Some fields limit your input to certain

values, and if you input data that is unacceptable, you will

hear a beep and will not be able to move from that field until

the correct data has been entered (or leave the field empty).

Some functions require that you select one data item from a

list. This is done by pressing a function key which pops up a

menu where you will select one item from a list of choices.

Use the UP or DOWN ARROW keys to position the hilighted bar

over your choice and press ENTER.

_________________________  Page 2  __________________________

After you have entered all required data, the calculation will

be performed and displayed. You can then change individual

data items and instantly see the results.

CAUTION:

When entering the last data item, or changing one data item

which was previously entered: Be sure to record that change by

moving from that field to another field, or by pressing ENTER

while still on that field.

Selecting Conductors

ELECTRC9 supports the new NEC 110-14(c) temperature limitation

requirements. Now when you press the function key which pops

up a list of available conductor types, there is also a

temperature rating associated with each conductor and a

location reference to help you choose. When you select a

conductor from the list, you are also choosing which

temperature rating that conductor will be 'USED AT' (which

column of 310-16 will be searched for ampacity). When

selecting a conductor, remember that the temperature rating of

the terminal or equipment must not be exceeded. If the

equipment is listed for use at 75 degrees C maximum, then you

must choose a conductor from the list with a rating that

doesn't exceed 75 degrees.

Setup Color Defaults

Initially the program starts up in black and white. Select

'Setup' from the main menu. Then select either Color Display

or Mono Display. Your choice will be saved to a disk file,

which will automatically be used for future program use.

BOX FILL & SIZING

Device Box Fill & Sizing

Determines cubic inch volume required for boxes, as per 1993

NEC section 370-16. Conductor size range is from #18 thru #6.

Free space (cu.in.) required for each conductor:

------------------------------------------------

# 18 .. 1.5     |    # 12 .. 2.25    |    #  6 .. 5

# 16 .. 1.75    |    # 10 .. 2.5     |

# 14 .. 2       |    #  8 .. 3       |

_________________________  Page 3  __________________________

Deductions are as follows:

* 1 or more fixture studs, cable clamps, or hickeys:

1 deduction for each type of fitting, based on the

largest conductor contained in the box.

* Each Strap containing 1 or more devices:

2 deductions, based on the largest conductor connected to

each device strap.

* Grounding conductors:

1 deduction, based on largest grounding conductor in box.

* Isolated Ground conductors:

1 deduction based on largest isolated ground conductor

in box.

Enter The Quantity Of Each Size Conductor Within The Box:

A conductor running thru the box with no splices or

connections within the box should be counted as 1 conductor.

A conductor originating outside the box and terminating within

the box should be counted as 1 conductor.

Conductors, no part of which leaves the box (example ... a

jumper or pigtail from a splice within the box to a switch,

outlet or fixture mounted on the box), should not be counted.

Answer the prompts for devices, clamps, fittings, ground

conductors, add'l ground conductors:

Count each mounting yoke or strap containing one or more

devices as 1. Example... one duplex outlet - count as 1. two

duplex outlets - count as 2.

The remaining prompts are self explanatory. Answer Y for yes.

There is no need to answer N for any prompts which would be

answered as 'no'. A blank field is interpreted as 'no'.

A quick reference table of standard metal boxes and their

cubic inch capacity is available for viewing at any time, by

pressing F2. The current screen will be saved, and the table

will be shown. When you wish to return to the previous screen,

press any key. A printout is available by pressing F10. See

the documentation for printing for details.

_________________________  Page 4  __________________________

Junction & Pull Box Sizing - Straight Pull

Calculates the minimum length, in inches, of pull and junction

boxes where raceways enter and leave the box at opposite ends.

If the wiring method is cable assemblies instead of raceways,

first determine the trade size conduit which would be

appropriate for the size and quantity of conductors in the

cable assembly, then use that conduit size.

If more than one raceway or cable enters and/or leaves either

end of the box, always use the largest size.

The method used to determine minimum box length for straight

pull: Eight times the trade diameter of the largest raceway.

The operation of this function is straightforward. Position

the hilighted bar over the largest raceway size for this

calculation, then press ENTER. The results will be displayed.

A printout is available by pressing F10. See the documentation

for printing for details.

Junction & Pull Box Sizing - Angle or U Pull

Calculates the minimum distance, in inches, between each

raceway entry inside a junction or pull box and the opposite

wall of the box, where raceways enter and leave the box at

angles. If the wiring method is cable assemblies, see the

explanation above, under 'Straight Pull'.

The method used to determine minimum distance for angle or U

Pull: Six times the trade diameter of the largest raceway,

PLUS, the sum of the diameters of all other raceway entries in

any one row on the same wall of the box. Use the row with the

largest total diameter of raceways.

A quick reference table of standard boxes and their cubic inch

capacity is available for viewing at any time, by pressing F2.

When you wish to return to the previous screen, press any key.

A printout is available by pressing F10.

_________________________  Page 5  __________________________

CONDUIT SELECTOR

The Conduit Selector allows you to quickly and accurately

determine the conduit size required for 1 or more conductors.

Calculations are based on the Dimensions and Percent Area of

Conduit and Tubing from table 4, and from Conductor Dimensions

as per Table 5 of the NEC. Maximum allowable percent conduit

fill is 53% for 1 conductor, 31% for 2 conductors and 40% for

more than 2 conductors, as per table 4.

Use the UP, DOWN, TAB or SHIFT+TAB keys to move the cursor to

the desired wire size/type position, then enter the quantity

of that size/type conductor to include in the conduit. If you

want to include other size/types of conductors into the same

conduit, then repeat the above procedure. You can enter any

combination of conductors in the same conduit.

NOTE: Several fields will show an asterisk ( * ). This

represents the unavailability of those sizes/types of

conductors. Do not alter those fields.

Pressing F2 at any time will show the results of the

calculation. The program will list all the sizes and types of

conductors you chose for the calculation, their individual

areas, the total area extensions, the grand total area for all

conductors, the minimum trade size conduit required, the total

area for the calculated conduit, and the percent conduit fill

for the calculation. If more data is available than will fit

on the screen, you will be able to use the UP and DOWN ARROW

keys to scroll through the data. Pressing any key will return

you to the conduit selector input screen with all previous

data intact. A printout is available by pressing F10. See the

documentation for printing for details.

_________________________  Page 6  __________________________

GENERAL CALCULATIONS

Cost To Operate

Calculates the cost to operate a certain load a number of

hours daily for some number of days at a certain KWH utility

charge.

POWER OF LOAD is the number of watts the load draws.

DAILY USE is the number of HOURS the load is operated per day.

NUMBER OF DAYS is the number of days the load is operated.

PRICE / KWH is the utility charge per killowatt hour.

(Example..  10 cents/kwh, enter .10)

NOTE: A value of ten cents/Kwk initially appears in the

'Price/Kwh' field, as an example only. You should change

this value to reflect your own price/Kwh charge.

After entering the above information, the program calculates

and displays the cost to operate the load for the number of

hours daily for the number of days at the chosen utility

charge. A printout is available by pressing F10. See the

documentation for printing for details.

Motor Amperes

A generic procedure to calculate motor amperage when hp, pf

and efficiency are known.

The calculation formula is:

1 phase:

(hp x 746) / (volts x pf x efficiency)

3 phase:

(hp x 746) / (1.73 x volts x pf x efficiency)

Simply enter appropriate values at the prompts for hp, pf and

eff. If pf and/or eff. is 100% or unity, enter 100 at those

prompts. Note that this procedure is not to be used in

determining motor full load amperage for the purpose of

calculating conductor, overcurrent or overload sizes. Use the

'Motor Calcs' function.

_________________________  Page 7  __________________________

Motor HP

A generic procedure to calculate motor horsepower when

voltage, amperage, pf and efficiency are known.

The calculation formula is:

1 phase:

(volts x amps x pf x efficiency) / 746

3 phase:

(1.73 x volts x amps x pf x efficiency) / 746

Simply enter appropriate values at the prompts for volts,

amps, pf and eff. If pf and/or eff. is 100% or unity, enter

100 at those prompts.

Amperes

Used to calculate amperes when va and volts, and pf are known.

The formula is:

1 phase:

va / (volts x pf)

3 phase:

va / (1.73 x volts x pf)

Simply enter appropriate values at the prompts for va, volts

and  pf. If pf is 100% or unity, enter 100 at that prompt.

Va

Used to calculate va when volts, amps and pf are known.

The formula is:

1 phase:

volts x amps x pf

3 phase:

1.73 x volts x pf

Simply enter appropriate values at the prompts for volts, amps and

pf. If pf is 100% or unity, enter 100 at that prompt.

_________________________  Page 8  __________________________

LIGHTING CALCULATION ( Zonal Cavity Method )

Calculates the quantity of lighting fixtures required to light

any room or area to any desired footcandle level.

The Illuminating Engineering Society (IES) has devised a

flexible and accurate method for calculating lighting

requirements, called the ZONAL CAVITY METHOD. This method

assumes that any room or area to be lighted is made up of

three cavities, the CEILING CAVITY, the ROOM CAVITY, and the

FLOOR CAVITY.

The CEILING CAVITY extends from the ceiling surface down to

the lighting fixture mounting level. If the lighting fixtures

are recessed or surface mounted then the value of the Ceiling

Cavity will be zero. If they are suspended some distance below

the ceiling then the value of the Ceiling Cavity is the volume

of space between the ceiling surface and the fixture mounting

level.

The ROOM CAVITY extends from the fixture mounting level down

to the work height level. The work height level is the

distance above the floor where the required quantity of

footcandles is to be maintained (usually desktop or work bench

level).

The FLOOR CAVITY extends from the work height level down to

the floor. If the required footcandles is to be maintained all

the way to the floor, then the Floor Cavity value will be

zero.

Every surface exibits a certain ability to reflect light.

Light colored surfaces reflect more light than dark surfaces,

so more light will need to be provided in a dark environment.

The degree of a surface's reflectivity is referred to as it's

Percent Reflection value. Percent Reflection can be accurately

measured with a reflectometer, or standard reflectance tables

can be referred to, such as the following:

TABLE FOR INTERIOR ILLUMINATION DESIGN

----------------------------------------

COLOR                % REFLECTION

----------------------------------------

Flat white               75 - 85

Ivory                    70 - 75

Buff                     60 - 70

Yellow                   55 - 65

Light tan                45 - 55

Light green              40 - 50

Gray                     30 - 50

Blue                     25 - 35

Red                      15 - 20

Dark brown               10 - 15

------------------------------------------

_________________________  Page 9  __________________________

The MAINTENANCE FACTOR is a value determined from the

anticipated maintenance of the fixtures and reflective

surfaces in the room or area. The intensity of illumination

produced by a lighting installation will depreciate after some

time due to lamp aging, and dust and dirt buildup. The

MAINTENANCE FACTOR is designed to adjust for this. Typical

values are from .5 to .8. (.5 for a poorly maintained

environment, .8 for well maintained).

Each lighting equipment manufacturer publishes data for the

COEFFICIENT OF UTILIZATION (CU) for each fixture type and size

in it's line. The CU of a fixture is a measure of it's

efficiency under specific conditions of room cavity values and

effective reflectance values.

The formulas used in the ZONAL CAVITY METHOD :

CEILING CAVITY RATIO = (5 * Hc (L + W)) / (L * W)

ROOM CAVITY RATIO =  (5 * Hr (L + W)) / (L * W)

FLOOR CAVITY RATIO = (5 * Hf (L + W) / (L *  W)

WHERE:

Hc = distance from ceiling to fixture level (in feet).

Hr = distance from fixture level to work height (in feet).

Hf = distance from work height to floor (in feet).

L = length of room in feet.

W = width of room in feet.

ROOM LENGTH and ROOM WIDTH values must be entered in FEET.

Decimal points are accepted (Ex. 125, 50.5, etc...).

CEILING HEIGHT and FIXTURE HEIGHT must also be entered in

FEET. Decimal points are acceptable.

WORK HEIGHT must also be entered in FEET. Decimal points are

acceptable. If you want the WORK HEIGHT to be equal to the

floor, simply enter zero.

FOOTCANDLE LEVEL is a measure of the intensity of light

falling upon a specific surface.

Values for Percent CEILING, WALL, and FLOOR Reflectances must

be entered as whole numbers (50, 80, etc...) Exact values can

be obtained by use of a reflectometer, or a standard table for

interior illumination design can be referred to, such as the

table for interior illumination design on the previous page.

_________________________  Page 10  _________________________

The value entered for MAINTENANCE FACTOR must be less than or

equal to 1. The value of between .5 and .8 will be accurate

for nearly all calculations. A value of 1 will exclude the

MAINTENANCE FACTOR from the lighting calculation.

NOTE:

A value of .8 initially appears in the 'Maintenance Factor'

field, as an example only. You can change this value to

reflect your own conditions.

To select fixture type, press F2. The menu will ask you to

select either 'built-in fixture type' or 'specify fixture

type'.

Built-In:

Fixture types stored internally include Recessed Incandescent,

Fluorescent, and High Intensity Discharge. COEFFICIENT of

UTILIZATION (CU) values which have been compiled by IES are

stored internally for these fixtures. The internally stored

fixtures are representitive of their types, as are the

internally stored lamp types. You will get accurate results

using them, but if you wish to use a type of fixture not

available internally, you can choose to specify your own type.

Specify:

If you choose to specify your own fixture type, you will be

prompted for the number of lamps per fixture, the quantity of

lumens per lamp, and, the coefficient of utilization (CU) of

the fixture. You will need to have the fixture manufacturer's

CU specs. LUMEN specs are available from various sources. Lamp

manufacturers will have lamp catalogs which will list LUMEN

values for their line of lamps.

After all data has been entered, the number of fixtures

required will be calculated and displayed. A printout is

available by pressing F10. See the documentation for printing

for details.

_________________________  Page 11  _________________________

MOTOR CALCULATIONS

Branch Conductor Sizing

Calculates motor branch circuit conductor size as per NEC

Article 430, Part B, and 430-6.

Conductor ampacity is based on 125 percent of motor full load

amperage (as determined from table 430-148 or 430-150),

multiplied by appropriate power factor multiplying factor,

multilpied by appropriate ambient temperature multiplier. This

product yields the 'Wire Ampacity Required' of the conductor

to be used to supply the motor. The program then selects the

conductor size of the type/temperature rating that you

specified that meets the required ampacity. This selected wire

size is verified by listing the ampacity (NEC Table 310-16) of

the calculated wire, and multiplies it by the ambient

temperature derating factor. This product yields the maximum

allowable ampacity of the selected wire. This value must equal

or exceed the 'Wire Ampacity Required' value calculated

previously.

21 conductor types/temperature ratings are supported. See the

section 'Temperature Limitations' in this file for more info.

Ambient temperature derating of conductors is also supported.

Fuse or Breaker Sizing

Calculates rating or setting of motor branch circuit

overcurrent protective device (Nontime-delay fuse, Time delay

fuse, Instantaneous trip circuit breaker & Inverse time

circuit breaker). NEC Article 430-Part D, and, 430-52.

Rating or setting is based on Full load amperage (from table

430-148 & 430-150) of motor, multiplied by appropriate power

factor multiplying factor, multiplied by appropriate

percentage factor from table 430-152 for the selected device

type. Article 430-52(a).

If this results in a value other than a standard size or

rating of overcurrent protection device, the next higher

standard rating is selected. Article 430-52(a), Exception 1.

_________________________  Page 12  _________________________

Overload Protection Sizing

Calculates motor overload protective device rating. Article

430, Part C.

Rating is based on motor full load amperage (from motor

nameplate) multiplied by:

125% if nameplate service factor is not less than 1.15,

or

125% if nameplate temperature rise is not over 40 degrees C.,

or

115 % for all others.

Access Keys Used To Select Motor Parameters:

Press:    To Select:              Press:    To Select:

--------------------              --------------------

F1        Help                    F6       Code Letter

F2        Motor Type              F7       Wire Type

F3        Start Method            F8       Ambient Temperature

F4        Phase/Volts             F9       Overcurrent Type

F5        Horsepower              F10      Print Report

NOTE:

The 'Percent Motor Power Factor', parameter is not an accurate

representation of true power factor. It is a VERY ROUGH item

that should be used with caution. At the 'Percent Motor Power

Factor' field, entering 100 will exclude the motor's Power

Factor from the calculation.

_________________________  Page 13  _________________________

PIPE & WIRE SELECTOR

Calculates the conductor size required to carry a certain load

for some distance while not exceeding a specific voltage drop

percentage, and the trade size conduit required to contain

those conductors.

21 conductor types/temperature ratings are supported. See the

section 'Temperature Limitations' in this file for more info.

Ambient temperature derating of conductors is also supported.

Conductor ampacity derating due to the number of current

carrying conductors in the raceway is supported as per NEC

310-Note 8(a).

Six circuit types are supported:

--------------------------------

1 Phase 2 Wire(Phase & neutral, or 2 Phase conductors)

1 Phase 3 Wire(2 Phase conductors & neutral)

1 Phase 3 Wire(Above circuit from a 4 wire wye system)

3 Phase 3 Wire(3 phase conductors)

3 Phase 4 Wire Wye(3 phase conductors & neutral)

3 Phase 4 Wire Wye circuit with the majority of load harmonic

In the third circuit type above, the neutral will carry

substantial current, and will be considered as a current

carrying conductor in the pipe size selection. NEC 310-Note

10(b).

In the last circuit type above, the neutral will carry

harmonic currents, and will be considered as a current

carrying conductor in the pipe size selection. NEC 310-Note

10(c).

Data Input

The 'Maximum Percent Of Voltage Drop' field will only accept

whole numbers in the range of 0 to 9. This will be the maximum

percentage of the supply voltage which can be dropped by the

circuit conductors. If you enter 0 in this field, voltage drop

will not be considered in the selection of the wire size.

'Full Load Amperage Of Load' is the rated or maximum amperage.

'Source Voltage' is the supply voltage for the circuit.

'Length of Run In Feet' is one way length from supply to load.

Access Keys Used To Select Circuit/Conductor Parameters:

Press:    To Select:         Press:    To Select:

-----------------------      -----------------------------

F1        Help               F4        Ambient Temperature

F2        Circuit Type.      F10       Print Report

F3        Wire Type.

_________________________  Page 14  _________________________

POWER FACTOR CORRECTION

Calculates the existing power factor and the capacitance

required to achieve a new power factor. The calculations are

accurate for single phase and balanced three phase conditions.

Do not rely on these calculations for situations where several

loads operate independently on the same feeder or branch

circuit, because the total power factor on the feeder or

shared branch circuit will vary, depending on which loads are

operating. Instead, run a calculation for each load

independently. Then, the calculated Kvars of capacitance

required should be installed as close as possible to the

individual load for which the calculation is performed. Also

note that if you improve the power factor of an existing

motor, the overload heaters should be changed to protect the

motor at the reduced amperage which will result.

Before considering the use of capacitance to improve power

factor, determine if the low power factor condition is caused

by the use of a motor that is oversized for the driven load.

Replacing the motor with a more efficient, properly sized unit

may be more practical and cost effective.

Power factor is the ratio of the true power (in watts) to the

apparent power (in voltamps). True power is measured with a

wattmeter. Apparent power is the product of volts and amps.

The result is the power factor of the load. For example, a

load is measured with a wattmeter and indicates 1880 watts.

The measured voltage is 240 volts. The measured current is 10

amps:

True Power          1800       1800

Power Factor = --------------- = ---------- = ------ = .75

Apparent Power    240 x 10     2400

The power factor of this load is calculated to be .75 (75%).

The apparent power (delivered power) of this load is 2400 VA

but the true power (useful power) is only 1800 watts. The

remaining 600 va are wasted in the form of heat losses.

Increasing the power factor would reduce the heat loss and

reduce the current requirements of the circuit supplying this

load.

To increase the power factor of an inductive load, capacitance

can be connected to the load. The required amount of

capacitance (in Kvars) must be calculated.

_________________________  Page 15  _________________________

The formula for determining existing PF and capacitance

required:

Single Phase - Existing:

Kva = (volts x amps) / 1000

PF  = Kw / Kva

Phase Angle = The angle that has a cosine equal to the PF

Kvars = Kva x SIN of the phase angle

Single Phase - Proposed:

Kva = Kw / Proposed PF

Line Amps = (Watts x 1000) / (Proposed PF x Volts)

Phase Angle = Angle with a COSINE equal to the proposed PF

Kvars = Proposed Kva x SIN of the proposed phase angle

Three Phase - Existing:

Kva = (volts x 1.73 x amps) / 1000

PF  = Kw / Kva

Phase Angle = Angle with a COSINE equal to the PF

Kvars = Kva x SIN of the phase angle

Three Phase - Proposed:

Kva = Kw / proposed PF

Line Amps = (Kw x 1000) / (Proposed PF x volts x 1.73)

Phase Angle = Angle with a COSINE equal to the proposed PF

Kvars = Proposed kva x SIN of the phase angle

Single and Three Phase:

Capacitive Kvars Required = Existing Kvars - Proposed Kvars

Recovered Distribution Losses = Existing Kva - Proposed Kva

NOTE:

Depending on computer processor speed, there will be some

delay in calculating the phase angles and the kvars. On a

486/33, it will be unnoticeable, while on an 8087 at 4.77 Mhz

it can take 15 seconds or so.

_________________________  Page 16  _________________________

PRINTING REPORTS

You can print reports either to a printer or to a disk file

for all functions except for the general calcs, and for all

Quick Reference Tables.

Printer support is generic (Printer Port LPT1 only), offering

no special print types, although you can set the desired print

type, size, etc, on your printer before printing the report.

Also supported is the printing of reports to an ASCII disk

file, for importing into your word processing program. For the

general calcs, you con do a 'Print Screen' to send output to

the printer. This can be done on most computers by pressing

the SHIFT key and the PRINT key simultaneously.

To print a report, press the F10 function key. You will be

prompted for a Job Name, Address, City & State, and

Description. These are optional and they may contain any data.

The data entered at these prompts will be printed at the top

of the report*. Next, enter P to print to a printer, or, D to

print to disk. When you are ready to print the report, press

F10.

NOTE:

To print any of the Quick Reference Tables, press F10 while

viewing the table. The 'Print' input screen allows input of

job name, address and description, however, this information

will not be printed to any of the Quick Reference reports.

Simply leave those fields blank.

NOTE:

When printing reports or Quick Reference Tables that are

longer than one page to printer, the program does NOT check

for page breaks. If you prefer, you can set your printer to

'Skip Perforation'. This will leave a margin at the bottom of

each page, and continue at the top of the next page.

QUICK REFERENCE TABLES

Equipment Ground Conductors

To determine the required size equipment ground conductor, as

per NEC Table 250-95.

Grounding Electrode Conductors

To determine the proper grounding electrode conductor size, as

per NEC Table 250-94.

_________________________  Page 17  _________________________

Kw To Amperes

To quickly convert single and three phase KW values to ampere

values and vice versa. Pressing PG UP & PG DN scrolls between

the single phase and three phase tables.

Underground Cover Requirements

To determine the minimum cover requirements of conduit,

underground cable, and other raceways, as per NEC Table 300-5.

Metal Device Boxes

Table of metal device boxes and their cubic inch capacities.

Standard Pull & Junction Boxes

Table of standard pull & junction boxes and their cubic inch

capacities.

Standard Fuses & Breakers

Table of standard ratings of overcurrent devices.

Transformer Kva To Amperes

To quickly convert single and three phase transformer Kva

values to ampere values and vice versa. Pressing PG UP & PG DN

scrolls between the single phase and three phase tables.

NOTE:

The data for this table is located in the ELECTRC9.DAT file,

and is read in by the program. This file must be located in

the same drive\directory as the main program file,

ELECTRC9.EXE.

Terminal/Conductor Temperature Limitations

The new requrements of the 1993 NEC Section 110-14(c).

_________________________  Page 18  _________________________

Conductor Ampacity

Allowable ampacities and ambient temperature derating factors

of NEC Table 310-16. Pressing PG UP & PG DN scrolls the table.

NOTE: The data for this table is located in the ELECTRC9.DAT

file, and is read in by the program. This file must be located

in the same drive\directory as the main program file,

ELECTRC9.EXE.

SHORT CIRCUIT CALCULATIONS - Point To Point Method

The point to point method is a method of calculating available

fault currents.

To calculate the available fault current at various points

throughout an electrical distribution system. You can start

with the available short circuit current at a source point

(secondary of a utility transformer for example), and

determine the fault current available at any point beyond that

based on the voltage drop due to wire impedance and the

inductive effect of the circuit. Capacative reactance is

negligible at 600 volts or less, and is ignored. Note that the

values of effective impedance calculated by the program are

valid at 75 degrees C, and at 85 percent power factor of the

circuit.

A maximum of ten points can be calculated, single and three

phase. Motor contribution is not presently supportrd in this

version of the software.

_________________________  Page 19  _________________________

Method used to determine available short circuit current at

any point:

1. Obtain the available short circuit current at your

starting point:

If your starting point is the secondary of a utility

transformer, the utility company should be consulted

for this information. If your starting point is a

transformer and fault current is not known, determine

the fault current available at the secondary terminals

as follows:

A. Calculate the Multiplier:

Multiplier = 100 / Percent Transformer Impedance

Example:

277/480v, 3 phase 500 Kva transformer Percent

nameplate impedance = 2 percent

Multiplier = 100 / 2

Multiplier = 50

B. Calculate short cct current at the secondary terminals:

Isca = Short circuit current at secondary terminals.

Isca = Transformer Full Load Amps x Multiplier

Example:

Isca = 500 amps x 50 'Multiplier from above'

Isca = 25000 amps

2. Calculate the C Factor:

C Factor = 1 / Wire Impedance Per Foot

Example:

500 kcmil copper conductor in steel conduit

From NEC Chapter 9, Table 9:

Impedance per 1000 feet = 0.050

Impedance per foot = 0.050 / 1000 = .00005

C Factor = 1 / .00005 = 20000

3. Calculate the F Factor:

L = One way conductor length from source point to the fault

I = available short circuit current at your starting point

C = C Factor

E = Line to line voltage at your starting point

NPC = Number of parallel conductors per phase

For 3 Phase Faults:

F Factor = (1.73 x L x I) / (NPC x C x E)

For 1 Phase Line to line faults:

F Factor = (2 x L x I) / (NPC x C x E)

Example:

277/480v, 3 phase source, I = 25000 amps,

150 feet #500 kcmil copper conductors, 1 per phase,

steel conduit, C = 20000

F Factor = (1.73 x 150 x 25000) / (1 x 20000 x 480)

F Factor = 6487500 / 9600000 = .6757813

_________________________  Page 20  _________________________

4. Calculate the M Factor:

M Factor = 1 / (1 + F Factor)

Example:

M Factor = 1 / 1.6757813 = .5967366

5. Calculate available short circuit current at the fault:

Short Circuit Current At The Fault = Isca x M Factor

Isca = available short cct current at your starting point

Ifsca = Short circuit current at the fault

Example:

Ifsca = Isca x M Factor

Ifsca = 25000 x .5967366 = 14918 Amps

Data Input And Calculation

The data input areas are where you will enter parameters for

the calculations. Use the UP ARROW and DOWN ARROW keys to move

from prompt to prompt. Using the ENTER key moves you down

through the prompts. Pressing the ESCAPE key aborts the

calculation and returns you to the main menu. An exception is

when you are selecting a choice from a group of options by

pressing one of the function keys. Pressing ESCAPE here only

backs you out of that selection area, and you do not lose any

data from the data input areas.

The first step in using the function is to input data at an

initialization area. Enter the number of points that you wish

to calculate fault currents for (maximum of 10).

Then press the PG DN key to access the data entry area for

point number 1 and proceed to enter data as follows:

Available Fault Current At Source - This will be the short

circuit amps available at the secondary of your utility or

distribution transformer, load side of main service

disconnect, etc, or wherever you choose to start the fault

calcs from. Note that if you are entering data for point

number 2, etc., The source would be the place where that point

is fed from.

One Way Conductor Length In Feet - The end to end length of

the wire run from the source to the location where the

available fault current will be calculated. Could be the mains

of the service equipment, line terminals of a panelboard, etc.

Use the one way length of one wire.

Number Of Parallel Conductors Per Phase - the number of

multiple conductors in parallel for each phase.

_________________________  Page 21  _________________________

Conductor Size - The Awg or Kcmil size of the wire. If the

wire size is # 4/0, input 4/0 at the prompt. For 750 Kcmil,

input 750. Acceptable wire range is from #12 to 1000 Kcmil.

Line To Line Volts Of This Point -  The voltage available at

the location where the fault current will be calculated. 600

maximum. Do not include any voltage drop in this value.

Single Or Three Phase -  Phase of this point.

Description - Optional field for whatever you wish to enter.

F2 - Press the F2 function key to select the wire material

(copper or aluminum) and raceway type (steel, aluminum, pvc)

used to supply this point. Note that raceway type also applies

to cable armor. Also, the calculations are based on three

circuit conductors in the raceway. If the circuit conductors

for the point being calculated are contained within a raceway

where other circuit conductors are present, the accuracy of

the calculation could not be assured.

Once all the above data has been entered, the results are

automatically calculated and the fault current amps is

displayed.

Pressing the F3 function key will show the details of the

calculation. The source current, the C Factor, F Factor, M

Factor, and the calculated fault current are displayed.

Pressing any key from the detail screen will return you to the

data entry area with all previously entered data intact. Note

that if you have not completely entered all required data for

at least one point, the F3 key will not work. Note that the

Description field need not be used, and leaving it blank will

not have any effect.

You can press PG UP or PG DN to scroll through the data entry

areas for each of the number of points that you inputted into

the initialization area. You can also PG UP until you are back

in the initialization area, change the number of points to

calculate, and PG DN through the areas without losing data.

However, if you change to a lesser number of points, you will

lose the data for the number of points greater than the newly

selected number of points.

A printout is available by pressing F10. See the documentation

for printing for details.

_________________________  Page 22  _________________________

TERMINAL/CONDUCTOR TEMPERATURE LIMITATIONS

NEC Section 110-14(c):

This new requirement of the 1993 NEC specifies the temperature

rules for termination of conductors. This requirement affects

every termination of conductors to electrical equipment. It

also includes separately installed pressure connectors such as

lugs. The intent is to protect connected equipment from

overheating due to the heat transfer that could result from

the connection of, for example, a 90 degree C conductor to a

terminal or device that has been tested and approved for use

at 75 degrees C. If the conductor were loaded so as to operate

at 80 degrees C, as long as it's ampacity was not exceeded, it

would not be damaged. However, if that same conductor was

connected to the terminal of equipment that was approved at 75

degrees C, the 80 degree heat transfer  could damage the

equipment or not allow the equipment to function as designed

and listed.

The basic rule is to provide two termination provisions for

conductors and connected equipment, and a third provision for

separately installed pressure connectors:

110-14(c)(1) - This first provision groups equipment for

circuits rated 100 amps or less, or equipment intended for

conductors from #14 to #1. This rule requires the use of the

60 degree C ampacity column of Table 310-16 for selecting the

conductors used to connect to this equipment.

Exception #1 permits the use of conductors with higher

temperature ratings only if they are sized in accordance with

their 60 degree C ampacity.*

Exception #2 permits the use of higher temperature rated

conductors at the ampacities of the higher rated conductors

only if the connected equipment is listed for use with the

higher rated conductors (such as a 100 amp breaker that is

listed for use at 60 or 75 degrees C, AND, the panel or

enclosure that the breaker is installed in is also listed for

use at the higher temperature).

110-14(c)(2) - This second provision groups equipment for

circuits rated over 100 amps, or equipment intended for

conductors larger than #1. This rule requires the use of the

75 degree C ampacity column of Table 310-16 for selecting the

conductors used to connect to this equipment.

Exception #1 permits the use of conductors with higher

temperature ratings only if they are sized in accordance with

their 75 degree C ampacity.*

_________________________  Page 23  _________________________

Exception #2 permits the use of higher temperature rated

conductors at the ampacities of the higher rated conductors

only if the connected equipment is listed for use with the

higher rated conductors.

110-14(c)(3) - Separately installed pressure connectors shall

be used with conductors at the ampacities not exceeding the

ampacity at the listed temperature rating of the connector.

Example:

Select feeder conductors for the following sub-panel, where:

The net computed feeder load is 60 amperes, the panel is

listed for connection at 60 degrees C. maximum, Type THHN

conductors are to be used, the ambient temp.is 30 degrees C.,

no derating required.

NEC 310-16, 60 degree C col. - #4 has an ampacity of 70 amps.

VOLTAGE DROP CALCULATOR

Calculates the voltage drop on existing or proposed single or

three phase resistive AC circuits (100% power factor). Copper

and aluminum conductors from #14 to 2000 Kcmil are supported.

The 'Single or Three Phase' is obvious.

The 'Length Of Run' is the length in feet of one conductor

from the source of power to the load terminals.

The 'Source Voltage' is the voltage measured at the source.

The 'Amperage Of Load' is the current required by the load.

For example, if the load is a resistance heater requiring 10

amps to operate as designed, then the AMPERAGE would be

entered as 10.

The WIRE SIZE is in the range of #18 Awg to 2000 Kcmil. Do not

include the # sign or the letters Awg or Kcmil. Enter the

numeric size of the wire (ex. 14, 1/0, 250, 750).

The COPPER or ALUMINUM prompt is self explanatory.

After entering the above values, the program will calculate

and display:

1. The VOLTAGE DROP of the circuit (the number of volts

dropped).

2. The VOLTS AT LOAD (the voltage delivered to the load

terminals)

3. The % DROP (the percentage of the source voltage dropped)

_________________________  Page 24  _________________________

OTHER ELECTRICAL SOFTWARE AVAILABLE

-----------------------------------

LOADCALC Copyright 1991 By Robert J. La Capra

Version 1.1

LOADCALC is designed to perform service/feeder load calcs for

single dwelling units. Full implementation of both the

Standard and Optional Calculation Methods of the 1990 NEC.

LOADCALC performs demand factoring, computes net computed load

in volt-amps and amperes, determines minimum service entrance

and feeder size.

Complete, professional printed reports. Send report data to

screen, printer, or to an ASCII disk file for import into your

word processor. Also prints up to 4 header lines of your

choice. Printer ports LPT1 and LPT2 supported.

LOADCALC operates with 'what-if' capability. You can quickly

and easily change only the data you wish to, without having to

start a new calculation and re-enter all the required data.

Results are calculated and displayed instantly.

Context sensitive help, describing the expected input, any

special definitions or requirements, and references to NEC

Article/Section, where applicable.

Quick reference tables for:

Grounding Electrode Conductor Sizes (NEC Table 250-94)

Service/Feeder Conductor Sizes      (NEC 310, Note 3)

* Standard Calculation Method:

Demand Factoring For:

General Lighting, Small Appliance and Laundry Loads.

Cooktop, Range, Wall Oven.

Fixed Appliances.

Largest Motor Load.

Additional User-Definable Loads:

2 add'l appliance loads, motor/nonmotor, fixed/nonfixed.

1 add'l lighting load, continuous/noncontinuous.

Automatic selection of larger of heating or cooling loads.

* Optional Calculation Method:

Demand factoring of 'other loads' as per NEC 220-30.

Allows input of heating system type per NEC Table 220-30, and

automatically determines larger of heating or cooling loads.

Additional User-Definable Loads:

2 additional appliance loads, 1 additional lighting load.

_________________________  Page 25  _________________________

Actual Printed Report From LOADCALC Version 1.1

STANDARD SERVICE/FEEDER LOAD CALCULATION - One Family Dwelling

Ralph Colbert

23 Maple Tree Lane

Byram Twsp., NJ 18539

Block 55, Lot 10

�������������������������������������������������������������������������������

General Lighting ... : 3200 Sq. Feet x    3 VA =  9600 VA

Small Appliance .... :    2 Circuits x 1500 VA =  3000 VA

Laundry ............ :    1 Circuits x 1500 VA =  1500 VA

---------------------------------------------------------

Total General Light & Small Appliance ........ : 14100 VA

The First   3000 VA @ 100%  =   3000 VA

Remaining  11100 VA @  35%  =   3885 VA

---------------------------------------

GENERAL LIGHTING, SMALL APPLIANCE & LAUNDRY DEMAND LOAD ..... :  6885 VA

Heating Demand ..... : 20000 VA @ 100% = 20000 VA

Cooling Demand ..... :  9000 VA @ 100% =  9000 VA

LARGER OF HEATING OR COOLING DEMAND LOADS (Heating) ......... : 20000 VA

Cooktop ................. :  4000 VA

Range ................... : 12000 VA

Wall Oven ............... :  5000 VA

COOKING EQUIPMENT DEMAND LOAD ............................... : 13850 VA

Dryer ................... :  5000 VA

DRYER DEMAND LOAD ........................................... :  5000 VA

Water Heater ............ :  6000 VA

Attic Fan ............... :  1000 VA

Compactor ............... :   800 VA

Dishwasher .............. :  1200 VA

Disposal ................ :   650 VA

Well Pump ............... :  1100 VA

------------------------------------

Fixed Appliance Total ... : 10750 VA

10750 VA @  75% Demand:  8063 VA

FIXED APPLIANCE DEMAND LOAD ................................. :  8063 VA

Largest Motor: Well Pump ............... : @ 1100 VA

25% OF LARGEST MOTOR LOAD ................................... :   275 VA

_______________________________________________________________________________

NET COMPUTED LOAD ........................................... : 54073 VA

120/240 VOLT SERVICE/FEEDER LOAD ............................ : 225 AMPERES

_________________________  Page 26  _________________________

Actual Printed Report From LOADCALC Version 1.1

OPTIONAL SERVICE/FEEDER LOAD CALCULATION - One Family Dwelling

Ralph Colbert

23 Maple Tree Lane

Byram Twsp., NJ 18539

Block 55, Lot 10

�������������������������������������������������������������������������������

General Lighting ... : 3200 Sq. Feet x    3 VA =  9600 VA

Small Appliance .... :    2 Circuits x 1500 VA =  3000 VA

Laundry ............ :    1 Circuits x 1500 VA =  1500 VA

Cooktop ...................................... :  4000 VA

Range ........................................ : 12000 VA

Wall Oven .................................... :  5000 VA

Dryer ........................................ :  5000 VA

Water Heater ................................. :  6000 VA

Attic Fan .................................... :  1000 VA

Compactor .................................... :   800 VA

Dishwasher ................................... :  1200 VA

Disposal ..................................... :   650 VA

Well Pump .................................... :  1100 VA

----------------------------------------------------------

Total Other Load ............................. : 50850 VA

The First  10000 VA OF Other Load @ 100% = 10000 VA

Remaining  40850 VA Of Other Load @  40% = 16340 VA

---------------------------------------------------

OTHER LOAD DEMAND LOAD ...................................... : 26340 VA

Heating Type:

One Central Space Heating Unit And/Or Supplimentary Unit In Heat Pump

Heating Demand Load ... :20000 VA @  65% = 13000 VA

Cooling Demand Load ... : 9000 VA @ 100% =  9000 VA

---------------------------------------------------

LARGER OF HEAT OR COOLING DEMAND LOADS [ Heating ] .......... : 13000 VA

_______________________________________________________________________________

NET COMPUTED LOAD ........................................... : 39340 VA

120/240 VOLT SERVICE/FEEDER LOAD ............................ : 164 AMPERES

LOADCALC REGISTRATION FORM

S1234

NOTE: THIS FORM TO BE USED TO REGISTER FOR "LOADCALC" SOFTWARE ONLY. Do Not

use to register for "ELECTRC9" software.

Registration fee for 1 to 5 users is $45.00 for each user or machine.

Site License & Multiple discounts available for 6 or more users. Write for info.

Purchase orders without payment attached cannot be accepted.

US funds drawn from a US bank only.

INCLUDED WITH YOUR REGISTRATION

Disk containing latest program version and documentation file.

Documentation is supplied on disk file. No printed manuals available.

One License To Use Software for each user registered.

Unlimited support by US Mail and by CompuServe Mail. No phone support available.

Shipping via US Postal Service. Orders shipped same day registration received.

OPTIONAL ITEMS

* UPS Ground Delivery - $10.00 additional per order. Multiple registrations or

registration of LOADCALC and ELECTRC9 together qualify as 1 order, and

shipping charge is $10.00 total. Supply street address. NO P.O. BOXES.

* 1 Year Of Fax Support for LOADCALC - $10.00 additional per year. For multiple

registrations of LOADCALC, fee is still $10.00 total.

Fax # supplied with shipment.

Return This Form And Registration Fee PAYABLE TO:

ROBERT J. LA CAPRA

50 Hillside Terrace

Andover, NJ 07821

S.S.# 137-44-7561

SHIP TO:

Name: ____________________________________________________________________

Company: _________________________________________________________________

Address: _________________________________________________________________

City,State,Zip: __________________________________________________________

Phone Number: ______-______-________    Fax Number: ______-______-________

Number Of Users: ______ x $45.00 Each = Registration Fee .. : $___________

UPS Ground Shipping Charge - $10.00 Per Order [Optional] .. : $___________

One Year Of LOADCALC Fax Support - $10.00 [Optional] ...... : $___________

__________________________________________________________________________

TOTAL FEE ENCLOSED .... : $___________

DISK SIZE PREFERRED:   [   ] 5 1/4"     [   ] 3 1/2"